## Slide 1: Simulator Lab Exercises for Kongsberg TPPS and Thermodynamics
Sanja Boskovic & Serhat Beyenir

## Slide 2: Overview
Simulator lab exercises (SIM LABS) support Thermodynamics and Thermal Power Plant Simulator (TPPS) courses
Built on Kongsberg’s TPPS platform
This session presents a selection of SIM LABS developed for classroom and lab use

## Slide 3: The Challenge
Power Engineering students often struggle with theoretical concepts
Instructors face limited instructional time to cover both theory and practice
A gap remains between classroom theory and hands on plant operation

## Slide 4: How SIM LABS Help
Strengthen understanding of core ThermoFluids principles
Support application of theory in realistic operational contexts
Allow students to visualize processes and explore system behaviour
Build cause and effect connections between operating parameters and outcomes

## Slide 5: Learning Benefits
Enhance conceptual comprehension
Prepare learners for hands on work with real equipment in a physical plant
Reinforce safe operational practices
Build environmental awareness within steam plant systems

## Slide 6: SIM LABS Featured in This Session
Boiler Efficiency
Turbine Efficiency
Power Plant Efficiency
NOx Emissions
Heat Exchangers
Combustion Analysis

## Slide 7: Boiler Efficiency: Objective and Theory
Operate the plant in four modes and compute boiler thermal efficiency: 230 MW burning HFO, 80% load burning biofuel, 80% load burning coal, and 80% load burning coal with soot buildup
Boiler thermal efficiency is the ratio of energy to steam over energy from fuel

## Slide 8: Boiler Efficiency: Lab and Deliverables
Four initial conditions: I10, I15, I14 (coal), and I14 with soot configured via MD250
Log HFO, pellet, and coal heating value tags, then use steam tables to find enthalpy values
Deliverables: trend plots for all four conditions, efficiency computations, and a conclusion comparing results

## Slide 9: Turbine Efficiency: Objective and Theory
Operate the plant at 35% load, 80% load, and 230 MW to compute the isentropic enthalpy change and thermal efficiency for the HP turbine
Turbine efficiency compares the actual enthalpy drop to the ideal, constant entropy expansion
A higher pressure drop in a single stage increases the reheat factor and lowers efficiency, which is why multi-stage turbines with reheat perform better

## Slide 10: Turbine Efficiency: Lab and Deliverables
Three initial conditions: I13 (35% load), I14 (80% load), and I10 (230 MW)
Compare results across conditions to determine which load yields the most favourable efficiency
Deliverables: trend plots for all three conditions, efficiency computations, and a conclusion with suggestions for further study

## Slide 11: Power Plant Efficiency: Objective and Theory
Operate the plant at full capacity and compute overall efficiency under three conditions: normal operation, high cooling water temperature (35°C), and without regeneration
The Rankine cycle efficiency is net work output over heat supplied in the boiler
Reheat and regeneration both raise the average temperature at which heat is supplied, improving efficiency over the simple Rankine cycle

## Slide 12: Power Plant Efficiency: Lab and Deliverables
Run initial condition I10 and draw a T-S diagram of the cycle including reheat and regeneration
Set cooling water temperature (tag T00305) to 35°C for the high temperature case, and to 10°C with extraction valves closed for the no regeneration case
Deliverables: T-S diagram, trend plots, efficiency computations for all three conditions, and a conclusion

## Slide 13: NOx Emissions: Objective and Theory
Operate the plant at full capacity and compare NOx emissions under five conditions: normal, OFA damper failure, OBA control failure, poor quality fuel, and DeNOx plant bypassed
NOx forms through two mechanisms: thermal NOx, which rises exponentially with flame temperature, and fuel-bound NOx, which depends on fuel nitrogen content
The DeNOx plant uses selective catalytic reduction with ammonia to remove NOx from flue gas

## Slide 14: NOx Emissions: Lab and Deliverables
Establish a stable operation baseline, then activate OFA malfunction 0881 and OBA malfunction 0780 in turn, switch to poor quality coal, and bypass SCR 1 and SCR 2
Tabulate percentage deviation from baseline for each condition
Deliverables: labelled trend plots, deviation calculations and plots, and a conclusion

## Slide 15: Heat Exchangers: Objective and Theory
Operate the plant at full capacity and study the effect of heat exchanger surface area using LP Feed Heater 3
Parallel flow heat exchangers have their largest temperature difference at the inlet, while counter flow heat exchangers maintain a more constant temperature difference along their length
Heat transfer depends on the heat area factor (UA) and the log mean temperature difference

## Slide 16: Heat Exchangers: Lab and Deliverables
Run initial condition I10 and vary the Heat Area Factor (tag C34201) across three levels: 0.5, 1.0, and 1.5
Run each setting for 15 minutes, then freeze and print trends
Deliverables: labelled trend plots for each setting, LMTD and effectiveness calculations, and a conclusion comparing the three tests

## Slide 17: Combustion Analysis: Objective and Theory
Operate the plant at 80% capacity burning coal to perform combustion analyses for two coal types and compare results
The stoichiometric combustion equation balances carbon, hydrogen, and nitrogen between fuel and air
Worked example: stoichiometric combustion of octane yields an air to fuel mass ratio of 15.25 kg air per kg fuel

## Slide 18: Combustion Analysis: Lab and Deliverables
Run initial condition I14 with default coal, then switch to poor quality coal using Variable List page 0111 on MD180
For both fuels, calculate total O2 required, stoichiometric air, product mass, and mass percentage of CO2, H2O, SO2, and N2
Compare furnace outlet SOx and NOx flow, CO and O2 content, theoretical combustion air, and coal heat value
Deliverables: labelled trend plots, combustion analyses for both fuels, and a conclusion

## Slide 19: Summary
SIM LABS bridge the gap between theory and practical plant operation
Six labs featured today span efficiency, emissions, heat transfer, and combustion topics
Each lab pairs a theoretical model with hands on simulator operation, reinforcing safe practice and environmental awareness

## Slide 20: Q&A